## AF-Calc
Arc Flash Calculator for Arcing Current and Incident Energy - to IEEE 1584 - 2002
Input data
Nom Voltage | V(kV) | 0.415 | Nominal Voltage
Fault Current | Ibf(kA) | 2.26 | Bolted three phase short-circuit current
Working Dist | D (mm) | 500 | Working distance between arc and worker's chest and face
AS 4836 = 500mm for 415V
Fault Clearing Time | t(s) | 20 | Relay tripping time plus breaker clearing time
Bus bar Gap | G=25mm | 25 | Distance between conductive parts
IEEE 1584 Table 2
Arc in box | K=-0.097 | -0.097 | Factor for arc in an enclosure
see IEEE 1584 section 5.2 equation 1
| log(Ia) | 0.24587 | Log ( arcing current )
Arc Current | Ia | 1.7614 | Arcing current
Arc in box | k1=-0.555 | -0.555 | Factor for arc in an enclosure
see IEEE 1584 section 5.2 equation 1
Grounded system | k2=-0.113 | -0.113 | Factor for arc in an enclosure
see IEEE 1584 section 5.2 equation 1
| log(En) | -0.37472 | Log ( Incident energy normalized for arcing time of 0.2 sec and
working distance of 610 mm )
| En | 0.42197 | Incident energy normalized for arcing time of 0.2 sec and
working distance of 610 mm )
Panel/SwGr distance factor | x=1.641 | 1.641 | See table 4 of IEEE 1584
LV factor | Cf=1.5 | 1.5 | Factor for Un =< 1.0 kV See equi 6 of IEEE 1584
IEEE - Inc Energy (J/cm2) | IEEE 1584 | 367.0113 | Incident Energy
IEEE - Inc Energy (cal/cm2) | IEEE 1584 | 87.7178 | Incident Energy
Lee Method - (J/cm²) | Lee Method | 160.7185 | Incident Energy
Lee Method - (cal/cm²) | Lee Method | 38.4127 | Incident Energy